## General
| Division of Responsibilities Matrix - MODULE ONE GENERAL X - Executes A - Approves H - Hold point - COMPANY Must Attend W - Witness - COMPANY is notified and COMPANY should make every effort to attend I - Inspect or Inform - COMPANY inspects through verification process S - Support |  |  |  | CONTRACTOR | COMPANY
[6 empty] | Construction Team | Project Commissioning Team | Owner's Operation and Maintenance Team | Project Management Team
A-1 | Commissioning Management Deliverables
A-1.1 |  | General
|  |  | Develop, issue and update the Commissioning Strategy, applicable to the project and to be approved by project leader |  |  |  | X
|  |  | Develop and issue Commissioning Readiness Plan |  |  |  | X
|  |  | Develop, issue and update Commissioning Execution Plan |  |  |  | X
|  |  | Develop, issue and update Commissioning Scope of Work and associated responsibilities |  |  |  | X
|  |  | Develop, issue and update the project contract self verification procedures including Subcontractors scope of work | [5 empty] | A
|  |  | Develop, issue and update the project COMPANY oversight Plan and Procedure | [5 empty] | X
|  |  | Report and action results of the self verification activities |  |  |  | X |  | A
|  |  | Report and action results of the COMPANY Oversight activities | [5 empty] | X
Commissioning Master Document Register (MDR), refer to attached COMPANY minimum requirements
|  |  |  | Develop and issue Commissioning Master Document Register (MDR) including all Commissioning deliverables to be produced/updated up to final Handover |  |  | X
|  |  |  | Include Commissioning MDR into the Project Master MDR |  |  | X
A-1.2 |  | Construction Completion Planning and Scheduling
|  |  | Develop and issue a Level II, III, IV and V time schedule consistent with the contractual Schedule/milestone showing the associated resources, in line with the Commissioning Scheduling requirements |  | X | A | A | I
The documents related to detailed time schedules shall be construed, prepared and transmitted as per below requirements:
|  |  |  | Detailed time schedules (from Level II to Level V) | X | A | A
|  |  |  | 90 days schedule | X | A
|  |  |  | 3 weeks look-ahead schedule | X | A | I
A-1.3 |  | Commissioning Planning and Scheduling
|  |  | Develop and issue a Level II commissioning schedule and provide the key system construction completion milestones |  | I | I | X | I | I
|  |  | Develop and issue a Level III, IV and V schedule showing the associated resources, in line with the Start-up scheduling requirements |  | I | I | X | I | I
|  |  | Develop and issue a Level III, IV and V schedule showing the associated resources, post RFSU, in the case owner led post RFSU |  |  | I | X | I | I
|  |  | Establish commissioning progress measurement and reporting to follow the Project System Handover Management Practice |  |  | I | X | I | I
The documents related to detailed time schedules shall be prepared and transmitted as per below requirements, depending on the contractual scheme:
|  |  |  | Detailed time schedules (from Level III to Level V) |  |  | X | I | I
|  |  |  | 90 days schedule |  |  | X | I
|  |  |  | 3 weeks look-ahead schedule |  | I | X | I | I
|  |  |  | Dedicated and detailed schedule for key equipment, such as: main gas compressors and the auxiliaries, utilities units such as air and nitrogen production units, etc. |  | I | X | I | I
A-1.4 |  | Organisation Charts & Mobilisation Plans
|  |  | Develop and Issue Static Commissioning Organisation Chart & Mobilisation Plans |  |  |  | X |  | A
|  |  | Develop and issue the CC Completion Team Organisation chart and Mobilisation Plan |  |  |  | X |  | A
|  |  | Develop and Issue Static and Dynamic Commissioning Organisation Chart & Mobilisation Plans |  |  | I | X | S | A
|  |  | Supply and Establish the Commissioning Campaign Room where daily/weekly alignment reviews will take place |  | S | I | X
A-1.5 |  | Alarm Management During Commissioning Phase
|  |  | Develop and Issue a strategy for managing alarms during Commissioning |  | S | I | X | I
A-1.6 |  | Gap Analysis
|  |  | Perform gap analysis and ensure project requirement alignment with ICA Global Commissioning Standard |  | X | I | A
A-2 | Deliverables requirements
A-2.1 |  | Procedures for Work to be Conducted Prior to CC
Construction Inspection and Test Plans (ITPs)
|  |  |  | Develop and issue construction ITRs and ITPs, incorporating the GAP analysis findings | X | A | I
|  |  |  | Develop and issue procedures to accompany the ITPs | X | A | I
A-2.2 |  | Static commissioning and Dynamic Commissioning Procedures
Static commissioning Procedures
|  |  |  | Develop and issue Standard Static commissioning Procedures to accompany ITRs, where applicable | S |  | X
Dynamic Commissioning Procedures
|  |  |  | Develop and issue Dynamic Commissioning Procedures for all Systems including packages, as applicable ( safety critical systems are identified and the commissioning procedure satisfies the performance standard), depending on the contractual scheme | S |  | X
A-2.3 |  | Safety Related Devices (SRD)
|  |  | Safety Related Devices (SRD) methodology to easily track and demonstrate the status and completion of Safety Critical Devices (SCD) Commissioning to support Start up assurance |  | S |  | X | I
|  |  | Ensure that performance standards required of safety related devices are either incorporated into the System Commissioning Procedures or covered by static commissioning activities documented in ITRs |  | S |  | X | I
A-2.4 |  | Procedures for modifications management
|  |  | Develop and issue Project Management of Change Procedure, to follow COMPANY Standards |  | X | I | I | I
|  |  |  | Within project MOC procedure, provide the project Control of Temporary Modifications Procedure to be followed (e.g. Temporary equipment / Temporary Spades / Blinds management ) to follow COMPANY Standards | X | I | W | I | A
|  |  | Develop and issue Temporary Change Control Procedure or any other software modification, to follow COMPANY Standards |  | X | I | A | I
A-3 | HSSE
A-3.1 |  | General
|  |  | Develop and issue Safety Transition Plan for the following phases, as a minimum: - Construction Phase - Commissioning phase - Simultaneous activities between Construction and Commissioning |  | S | S | X | I
A-3.2 |  | Control of Work (CoW) and Permit to Work (PTW)
Issue Control of Work (CoW) and Permit to work (PTW) procedure
|  |  |  | during Construction | X | A | A | I
|  |  |  | during Static commissioning and Dynamic commissioning | S | S | X | S | S
|  |  | Supply and installation of any temporary fencing for commissioning or start-up purpose, for CoW requirements |  | X
Permit to Work (PTW) Audit Programmes:
|  |  |  | Develop and issue PTW Self-Audit Programme |  | I | X | I | I
Permit requirements
|  |  |  | Provide trained and competent sufficient resources for the tasks of permit coordinator, permit auditor, electrical isolation authorities, etc. | S | I | X | S
|  |  |  | Provide sufficient mobile offices, printers, computers, isolation tags, etc… | S | I | X | S
|  |  |  | Provide the proper trainings for the CoW and PTW applicable to the project different phases | X | I | X | S
A-3.3 |  | Energization of Systems
|  |  | Develop and issue Energisation and Livening Up Procedures |  | I | I | X | S
|  |  | Develop and issue Energy Isolation Procedure(s) |  | I | I | X | S
A-3.4 |  | Isolation Material requirements
|  |  | Prepare a detailed list of the isolation material to be procured and made available by CONTRACTOR, up to CONTRACTOR Scope of Work completion, e.g. blinds. |  | X |  | A
|  |  | All isolation material (type and quantity), master keys, padlocks, tags, LOTO equipment for piping and electrical items, register to be validated by COMPANY, prior to procurement. Such material will be transferred to COMPANY during COMPANY commissioning and start-up activities up to operations handover phase |  | X |  | A
A-3.5 |  | Rigging and Lifting
|  |  | Develop rigging and lifting plans as required to support commissioning field execution activities according to the project requirements. |  | X | A | I
A-4 | System Completion and Handover Management
A-4.1 |  | General
|  |  | CONTRACTOR to use COMPANY completion management software for all the project. CONTRACTOR may propose, for COMPANY review and approval, use of any in-house completion tool, at CONTRACTORs own risk and responsibility. COMPANY to review CONTRACTOR proposal and full gap analysis prior to approval. |  | X | I | A
|  |  | Complete any additional requirements to ensure proper software communication, download/upload, updates, etc, between COMPANY completion tool and CONTRACTOR in-house completion tool. |  | X | I | A
A-4.2 |  | System Completion and Handover Documentation Management
|  |  | Develop and issue System Handover Management Procedure |  | S | I | X
|  |  | Ensure that Vendor Quality Plan for all packaged equipment covers all COMPANY requirements, including the System Completion and Handover Management requirements which are applicable to main project. Applies to all vendors under CONTRACTOR supply and to COMPANY supplied equipment after transfer to CONTRACTOR custody and control. |  | X | I | A
|  |  | Coordination and monitoring of completion process |  | S |  | X
|  |  | Set-up, tune and populate completion database to fit with project requirements during engineering phase and ensure the continuous update until the final handover (including compilation of engineering lists). |  | S | S | X
|  |  | Assign ITR's to tagged equipment and systems as per matrix |  | S | I | X
|  |  | Provide 7-day look-ahead of CC Walkdowns |  | X | I | I
|  |  | Issue CC walkdown pack (pack to be detailed on the completion procedure) 3 days prior to the planned CC Walkdown date |  | X | I | I
|  |  | Issue formal notification of CC Walkdown, 48 hours in advance of the Walkdown or as per project procedure requirement, ensuring safe access and sufficient time in schedule for the Walkdown |  | X | I | I
|  |  | Conduct Completion – Punching Walk downs for CC |  | X | H | H
|  |  | Issue RFDC Walkdown pack advance of RFDC system Walkdown date. |  | I | I | X | I
|  |  | Conduct RFDC Walkdown |  | S | S | X | H
|  |  | Provide 7-day look-ahead of System Handover Walkdown |  |  | I | X | I
|  |  | Issue System Handover walkdown pack prior to the planned System Handover Walkdown date |  |  | I | X | I
|  |  | Conduct Completion – Punching Walk downs for SH |  | S | S | X | H
|  |  | Develop and issue all System Handover Dossiers |  | S | A | X | A
|  |  | Resource the completion and handover team to ensure full project dossiers preparation, walk-downs and certification, according to COMPANY approved completion and handover system requirements |  | S | S | X | I
|  |  | According to the Completion and Handover management procedure, prepare daily/weekly completion reports |  | I | I | X | I
A-4.3 |  | Limits of System Handover (LOSH)
|  |  | Based on COMPANY provided System Handover LOSH, develop detailed system and subsystem LOSH mark-ups and maintain according to the latest revision of the Engineering documents (red mark-up) for all disciplines, e.g. electrical, piping, instrumentation and control, telecom, mechanical, hvac, etc... |  | I | I | X | I
A-4.4 |  | SHM Training and Competency
|  |  | Provide training and competency certification in the use of COMPANY Completions Module or other COMPANY approved Completion System for all staff (COMPANY, CONTRACTOR, and subcontractors) as required |  | I |  | X
|  |  | Manage the database access, according to the procedure in place and upon COMPANY agreement |  | I | I | X
A-4.5 |  | Punch listing Management
|  |  | Punch list close out, according to project punch list management procedure |  | X | W | H | H
A-5 | Construction Completion and Handover report templates
A-5.1 |  | System Construction Completion and Handover Report
|  |  | Prepare and issue Systems Construction Completion and Handover Report content and format template |  | I | I | X
A-5.2 |  | Commissioning Daily/Weekly /Monthly Report
|  |  | Prepare Commissioning Daily/Weekly /Monthly Report content and format template |  | I | I | X
A-5.3 |  | Commissioning Weekly Status Progress Report:
|  |  | Issue Commissioning Weekly Status Progress Report, including the following : |  | I | I | X | I
A and B ITRs Status Report by discipline by subsystem, like key activities: loop checks, Leak tests, Critical safety devices tests, etc.)
Construction Completion Skyline by sub system
Ready for Dynamic Commissioning (RFDC) Skyline by sub-system/system
System Handover Skyline by System
Punchlist Status Report
Preservation and Maintenance report
Deliverables issuance report
A-5.4 |  | Monthly Commissioning Progress Report
|  |  | Issue Monthly Commissioning Progress Report |  | I | I | X | I
A-5.5 |  | Commissioning Close Out Report
|  |  | Issue Commissioning Close Out Report |  |  |  | X | I
A-6 | Engineering Interface and Technical Support
A-6.1 |  | During Engineering Design Phase
Provide competent commissioning representation in design reviews including, but not limited to:
|  |  |  | BOD Reviews (basis of design content) |  |  | X
|  |  |  | HAZID |  |  | X
|  |  |  | HAZOP |  |  | X
|  |  |  | Model Reviews |  |  | X
|  |  |  | P&ID Reviews |  |  | X
|  |  |  | Other design reviews as required (SLD's, HVAC, etc.) |  |  | X
|  |  | Identify and integrate commissioning requirements into design (such as start-up strainers, isolation, bypasses, isolation valves, etc.) |  |  |  | X
|  |  | Provide competent and qualified personnel as required to support the preparation of Commissioning deliverables during the detailed design phase |  |  |  | X
A-6.2 |  | During Execution Phase
Discipline Engineering Support
|  |  |  | Provide competent and qualified discipline engineers up to final handover phase, according to contractual requirements | X |  | A |  | A
|  |  |  | Follow-up and closeout of Technical Queries / Clarifications raised by COMPANY | X |  | A |  | A
|  |  |  | Provide a dedicated engineering site team (including, but not limited to, competent and qualified systems engineers retained from the detailed design phase) | X |  | A |  | A
|  |  |  | Remedy, monitor and record any instrumentation and control defects arising during the commissioning phase | X |  | I | I | A
|  |  |  | Prepare and update Red-Line Mark-ups until final handover phase, for CONTRACTOR and VENDOR drawings | X |  | I | I | A
A-7 | Vendor Interface
A-7.1 |  | Vendor Information
|  |  | Obtain all required deliverables, additional information and/or assistance from suppliers (e.g. as required to develop preservation, maintenance, commissioning, start-up and operations procedures) |  | X |  | I | I | A
|  |  | Record and Track of all supplier / vendor materials related to commissioning spares, special tools, etc. |  | X |  | I | I
|  |  | Design, fabricate and install any temporary pipe spool required for dynamic commissioning activities, prior to CC completion |  | X | I | I |  | A
|  |  | Schedule and obtain all regulatory or verification certification, depending on the project region applicable rules and regulations |  | X |  | H | H | A
A-7.2 |  | Factory Acceptance Testing (FAT) & Integrated Factory Acceptance Testing (IFAT)
|  |  | Develop the required FAT & IFAT deliverables for the project, refer to Comm Doc Deliverables |  | X |  | A | I | A
|  |  | Develop the FAT/IFAT attendance matrix |  | X |  | A |  | A
|  |  | Attend FATs & IFATs as outlined on FAT/IFAT attendance matrix |  | X |  | W |  | W
A-7.3 |  | Vendor or COMPANY Supplied Items - Support
|  |  | Prepare and Issue the order for additional vendor Mobilisation, according to the required schedule completion plan (for construction assistance, commissioning assistance and start-up assistance), respective costs to follow project contractual requirements |  | X | A | A | A | A
|  |  | Prepare a Vendor Activity, Scope and Mobilisation Schedule (VASMS) for static commissioning, dynamic commissioning, start-up up to performance test |  | S | A | X | A | A
|  |  | Obtain vendor engineering support as required to support commissioning field execution activities including start-up phase |  | S |  | X |  | A
|  |  | Obtain vendor specialist support to repair any defect or damage and ensuring the warranty continuity and validity, as required |  | S |  | X |  | A
A-8 | Preservation and Maintenance
A-8.1 |  | Activities Definition and Execution
|  |  | Develop the Project preservation strategy and cleanliness requirements |  |  |  | X
Personnel, Tools, Consumable and Equipment for Preservation
|  |  |  | Assign CONTRACTOR preservation and cleanliness Lead | X | I | A
|  |  |  | Assign CONTRACTOR Preservation resources to the project | X | I | A
|  |  |  | Appoint a dedicated SUBCONTRACTOR team of competent personnel to perform preservation activities | X | I | I
|  |  |  | Supply all tools, materials and consumables required to perform preservation and maintenance activities | X
Preservation and Maintenance Procedures
|  |  |  | Develop and issue preservation and maintenance procedures incorporating supplier recommendations | X | I | A | I
Preservation and Maintenance Database
|  |  |  | Populate, maintain and update the Preservation database, as per COMPANY requirements | X
|  |  |  | Issue weekly preservation reports | X | I | I | I
|  |  |  | Conduct fortnightly preservation site walk-downs (with associated debrief meetings). Inform COMPANY 2 days prior to Walkdown. | X |  | W | W
Preservation Activities
|  |  |  | Supply any consumables/people and execute preservation of all equipment and systems during all the phases of the project (storage, during construction, during static commissioning and commissioning including start-up) until final handover | X
|  |  |  | Preserve and maintain the condition of all spare parts and special tools until final handover | X
|  |  |  | Conduct and record regular inspections of equipment and devices in storage | X
|  |  |  | Record and rectify all defects identified during preservation activities | X | I | I | I
A-9 | Housekeeping
A-9.1 |  | Applicable throughout Field Execution
|  |  | Supply all access and equipment, tools, and consumables required to support housekeeping activities |  | X
|  |  | Perform construction clean-up, including rough sweeping, refuse pick-up, removal of excess materials, waste chemicals and liquids and temporary facilities. (Includes offsite disposal) |  | X
|  |  | Clean-up construction debris |  | X
|  |  | Waste management for COMPANY activities, such as first filling activities, chemical cleaning (if under COMPANY responsibility) |  | X
A-10 | Inspection
A-10.1 |  | Applicable throughout Field Execution
|  |  | Provide COMPANY with notice of all inspections as per the introduction section of this document, informatic notification is acceptable |  | X | I | I | I
Perform inspection activities according to approved ITPs using approved ITRs, including but not limited to:
|  |  |  | Conformity checks of all assembled / erected facilities (incl. vendor skids) against IFC drawings | X | W | W
|  |  |  | Code stamps and other special inspections as required | X | W | W
|  |  |  | Positive Material Identification on non-carbon steel (including material marking and alloy verification) | X | W | W
|  |  | Provide competent and qualified personnel to re-open and close shop-inspected equipment for field inspection as required |  | X
|  |  | Some Systems and Sub-systems are non-functional. These are referred as Non-Commissionable Systems and Sub-systems and are typically related to: • Structures, jackets, Buildings, shelter. • Civil works: Concrete supports, bridge, fencing, etc. • Geographic Zone like: Escape routing, Upper deck, helideck, 1st Floor corridors, etc. These Non Commissionable Systems and Sub-systems shall still be subject to QA / QC Inspection & related ITPs, static commissioning and any regulatory certification, as applicable. |  | X |  | W
A-11 | Subcontracting and Specialist Services for Commissioning
Note: Individual specialist services (e.g. chemical cleaning and leak testing, etc.) are detailed elsewhere. This section covers the coordination and management of these services only.
A-11.1 |  | Develop Commissioning Subcontracting Management Plan
|  |  | Implement a proactive approach toward subcontractors’ safety requirements, training, material, Quality and delivery performance and develop a recovery plan for any shortfalls. |  | X |  | I |  | A
|  |  | Provide all specifications and detail, within the contractual scope, all the temporary means available with CONTRACTOR for the project execution, e.g.: air compressors capacity, air dryers data sheet, nitrogen production unit ratings and specifications, temporary pumps ratings available, temporary power generators, Load banks, etc..) |  | S |  | X |  | A
A-11.2 |  | Assistance to Dynamic Commissioning, Start-up activities or any other scope under CSU Team
|  |  | Support any Specialised services, hired by COMPANY, during the Mobilisation, implementation and until Demobilisation by providing all means of transportation, CoW, certifications, access control, safety requirements and personnel induction and project training |  | S |  | X
|  |  | Define Specialised services requirements for Commissioning Field Execution phase (e.g. leak testing, chemical cleaning, lube oil flushing, hydro milling, specialised cleaning, first fills, etc.) |  | S |  | X
|  |  | Provide duly qualified and trained SUBCONTRACTOR resources according to COMPANY CSU Team requirements, under an assistance agreement and time sheet basis |  | S |  | X
|  |  | Define any temporary equipment mobilised for the project, by CONTRACTOR, required for start-up and to be transferred to COMPANY |  | S |  | X | I | A
A-12 | Tie-Ins
A-12.1 |  | Applicable throughout Field Execution
|  |  | Follow Construction Completion (CC) and System Handover ( SH) process, as per project completion and handover quality requirements, for each and every tie-in/interface. |  | X | A | A | A | A
A-13 | Spares, Tools, Equipment, First Fills and Consumables
A-13.1 |  | Plant Consumables and First Fills
|  |  | Supply first fills for plant consumables, chemicals, lubricants, etc., as per the project contractual requirement |  | X |  | A | I | A
|  |  | Perform first fills as per the agreed scope, taking all the safety precautions and as per MSDS. |  | S |  | X | I | I
A-13.2 |  | Commissioning Spares
|  |  | Identify, procure and track the project required Commissioning Spares |  | X |  | A
|  |  | Upon shipping to site, ensure that commissioning spares are boxed up separately and provided with a detailed packing list. Packing list shall include part numbers (if applicable), detailed descriptions and quantities (no percentages or "lots" to be used in quantity descriptions) |  | X |  | I
|  |  | Commissioning spares must be stored and preserved separately from remaining project materials, and ensure that their issuance / use is approved by Commissioning Manager (CONTRACTOR and COMPANY) |  | X |  | A
A-13.3 |  | Commissioning Special Tools
|  |  | Identify and supply special tools required to support commissioning field execution activities |  | S |  | X | I
A-13.4 |  | Other Support, Materials, Tools and Equipment Required to Support Commissioning Field Execution
|  |  | Record all the Commissioning tools, spare parts and first fills thru the project material management control software |  | X | A | A |  | A
|  |  | Develop and issue the required project material management procedure and based on that: |  | X | A | A |  | A
|  |  |  | Provide suitable storage, preservation consumables and materials handling tools, according to approved procedures | X | A | A
|  |  |  | Ensure materials are managed thru the project tracking process for approved material control and issuance process | X | A | A |  | A
|  |  |  | Prepare and execute the handover between Storage warehouse and COMPANY Ops. Maintenance Warehouse, for all the commissioning and start-up material and tools | X | I | A | A
|  |  | Supply all tools and equipment (mechanical, electrical, instrumentation, HVAC, etc.) required to support commissioning field execution activities |  |  |  | X
|  |  | Supply all commissioning consumables (including diesel) required to support commissioning field execution activities. Monitor shelf life. |  | S |  | X | S
|  |  | Supply all scaffolding/access equipment and labour as required to support commissioning field execution activities, in case it falls under assistance scope, time sheet applies and COMPANY shall approve prior to erection |  | X | A
A-14 | Temporaries
A-14.1 |  | Temporary requirements for Mechanical
|  |  | Develop a project guideline for temporary material identification and management, applicable to all phases of the project. (e.g. storage, construction, commissioning, sea transport, etc.) |  | X | I | I |  | A
|  |  | Remove temporary supports, bracing or other objects installed in equipment to prevent damage during shipping, storage, commissioning and/or erection |  | X | I
|  |  | Provide engineering services to design temporary pipework, fittings, connections, etc. required to support commissioning field execution activities |  | X |  | I |  | A
|  |  | Supply temporary material such as: piping, fittings, connections, valve, etc. required to support commissioning field execution activities |  | X |  | I |  | A
|  |  | Enough hoses, fitting, flanges, gauges, quick opening valves, spare small bore valves for static commissioning activities |  | S |  | X
|  |  | Enough material for sailway preservation purpose, if applicable (such as: end caps for piping with pressure gauges for preservation control, nitrogen bottles, nipples, end flanges with nipple connections, etc…) |  | S | S | X
|  |  | Provide proper facilities and resources (manpower, lifting devices, etc..) for repairing activities for any damage or defect (such as valves seats lapping, pumps seals, valves dismantling, etc…) |  | X |  | S |  | A
A-14.2 |  | Temporary Utilities and Power
|  |  | Design and Supply temporary power supply and load banks required to support construction and commissioning works up until start-up |  | X | I | I
|  |  | Design and Supply temporary utilities required to support construction and commissioning works up until start-up |  | X | I | I
|  |  | Testing of all temporary utilities required to support construction and commissioning works up until start-up |  | X | I | S
|  |  | Air compressors and dryers |  | S | I | X
|  |  | Nitrogen production unit |  | S | I | X
|  |  | Water maximum availability and quality |  | S | I | X
|  |  | Power generators |  | S | I | X |  | A
|  |  | Power banks |  | X | I | I |  | A
|  |  | Lube oil flushing skids |  | X | I | I
|  |  | Dedusting skids |  | X | I | I
A-14.3 |  | Specific Temporaries requirements
|  |  | Supply temporary weather protection as required, during the full duration of the project |  | X | I
|  |  | Supply, install, test and obtain required regulatory certification for Temporary navigation equipment, e.g. lighting, SOLAS and maritime security, etc. |  | X | W | W
|  |  | Commissioning and Decommissioning of all the temporary equipment |  | S | S | X
|  |  | Supply, install and test all temporary equipment required for towing, e.g. lines bollards |  | X | W
A-15 | Warranty and Defect Handling
A-15.1 |  | Warranty and Defect Handling Team
|  |  | Provide a dedicated competent Warranty and Defects Handling team, with a dedicated Warranty Manager |  | X | A | A | I | A
|  |  | Supply all necessary materials including, but not limited to, replacement parts, construction materials, consumables, scaffolding support, tools and equipment (incl. cranes, air compressors and man-lifts), etc. required to remedy defects at the responsible entity cost |  | X | A | A | I | A
|  |  | Provide all engineering support required to remedy defects |  | X | I | A | I | A
|  |  | Identify construction defects and raise remediation request as well raise a punch item within completion and handover management tool |  | X | A | I | I | A
|  |  | Remedy construction defects and close-out remediation request |  | X | A | I | I | A

## Discipline
| Division of Responsibilities Matrix - MODULE TWO DISCIPLINE SOW X - Executes A - Approves H - Hold point - COMPANY Must Attend W - Witness - COMPANY is notified and COMPANY should make every effort to attend I - Inspect or Inform - COMPANY inspects through verification process S - Support |  |  |  |  | CONTRACTOR | COMPANY
[7 empty] | Construction Team | Commissioning Team | Owner's Operation and Maintenance Team | Project Management Team
GEN | General, it is understood that for all items within the DoR, the below bullets apply:
|  | Erect, assemble, install and preserve equipment in accordance with project specifications and vendor guidelines |  |  |  | X | W
|  | Inspect and perform systems cleaning, remove any preservation compounds, greases and oils from surfaces used to preserve the equipment during construction, prior to CC |  |  |  | X | W | I
B-1 | Piping
B-1.1 |  | Build it Clean (BIC)
|  | Define cleanliness requirements by commodity/system to be followed during construction phase |  |  |  | X |  | A
Scope requirements
Personnel, Tools and Equipment
|  |  |  | Provide a Cleanliness Assurance Team to implement the requirements of the Piping cleanliness assurance and verification process |  | X | A | A
|  |  |  | Supply all inspection tools, specific tools and materials, consumables required to perform cleaning activities |  | X | W
General Requirements
|  |  |  | Ensure that all open ends of piping and equipment are covered at all times when work is not taking place |  | X | W | I
Cleanliness Requirements during Preservation
|  |  |  | Verify that all piping and equipment has appropriate end covers securely fastened prior to shipping to site. |  | X | W | I
|  |  |  | Verify that all piping and equipment has appropriate end covers at the time of receipt from suppliers. If missing, verify that internal debris is removed, then reinstall the end cover. |  | X | W | I
Piping Erection
|  |  |  | Inspect and clean piping prior to erection |  | X | W | I
|  |  |  | Perform visual internal and external inspection to verify cleanliness, then reinstall piping end caps to any open ends after pipe spool is erected / secured to Piperack |  | X | W | W
Cleanliness Surveillance
|  |  |  | Perform continuous cleanliness surveys (e.g. including items such as piping make-ups (if available), end cover removals and inspections, random openings and inspections of fabricated pipe spools and straight run pipe, documenting the number of missing end covers, etc.). Communicate results to the Site QC Manager |  | X | W | W
|  |  |  | Perform boroscopic inspections to verify the cleanliness |  | X | W | W
B-1.3.3 |  | Pipe Cleaning - Construction Completions
|  |  |  | Identify all the cleaning packs for the project by preparing all the method of statements and cleaning path P&ID mark-ups. |  | X | I | A
|  |  |  | Prepare and supply all the temporary material required to each type of cleaning activity, as per piping project specification. No temporary material shall be accepted if its not proven fit for purpose. |  | X | I | A
|  |  |  | Perform cleaning operations according to the project approved procedures, prior to final piping reinstatement |  | X | W | H
|  |  |  | Remove and dispose of all test media from piping and equipment in accordance with waste management procedure |  | X | I | I
B-1.2 |  | Special Cleanliness Requirements for Interfaces
|  |  |  | Follow and Execute Cleaning for all project interfaces according to the defined scope of work and above build it clean requirements |  | X | I | W
B-1.3 |  | Pressure Strength Testing, Pipe Cleaning, Flange Management and Leak Testing
General
|  |  |  | The following items are valid for all packs to be prepared and executed: |  | X | I | I
[5 empty] | Develop the testing plan and associated tags for all tests, prior to CC. Include definition of test media, test pressures, etc. Produce a Tracking document with all the disciplines that should input until completion of the pack | X | A | I
[5 empty] | Develop the Cleaning, tightness test and drying plan and associated tags. Include definition of media, temporary material requirement, etc. Produce a Tracking document with all the disciplines that should input until completion of the activity | X | A | A
[5 empty] | Prepare, supply and fabricate all the required temporary spools/connections and equipment to perform piping strength test as well pipe cleaning, drying, tightness test and preservation activities. Ensure that all temporary equipment is duly suitable for usage and it follows the piping rating permanent requirements. | X | W | W
|  |  |  | Prepare and maintain a tracking list for all permanent used test blinds required / installed (including locations) for all activities, prior to CC |  | X | A | W
|  |  |  | Prepare, supply and execute all the temporary means to execute all the activities here mentioned, such as: hoses, couplings, gauges, fittings, quick opening valves, etc. |  | X | A | A
B-1.3.1 |  | Flange Management
|  |  |  | Ensure all flange management crews are trained and have the right competency level to perform the flange management activities according to the project expectations |  | X | W
|  |  |  | Develop the project Flange Management procedure. |  | X | A | A
|  |  |  | Define and implement flange management data base to support handover |  | X | A | A
B-1.3.2 |  | Pressure Strength Testing
|  |  |  | Identify the strength test requirements, hydraulic or pneumatic, according to the Process needs and as per the code requirements. If any change is required to the early defined pressure test media, CSU and process team approval is required. |  | X | A | A | I
|  |  |  | Develop the testing plan and tracking register for hydrostatic/pneumatic strength test time schedule, per Subsystem and according to the process needs |  | X | A | I
|  |  |  | Perform pipe cleaning and inspection, prior to the pipe strength test, according to project approved procedure. Perform visual and/or boroscopic inspection to ensure pipes are free of scale, dust or any other debris. Clean and re-inspect any lines found dirty, and document according to the project approved procedures. |  | X | W | H
|  |  |  | Prepare system for strength test (includes removal of sensitive inline fragile devices and/or equipment's) and installation of any temporary item for the testing purpose. Whenever the use of project permanent blinds are required, this must properly documented and accepted by Commissioning team, refer to attach.1 applicable deliverables required to be issued. |  | X | W | I
|  |  |  | Perform hydrostatic/pneumatic strength tests according to approved procedures |  | X | W | I
|  |  |  | Note: Remove, dispose and dry all (DP<-1degC, as a minimum, or as per project approved procedure) test media from piping, in accordance with the project approved procedures. |  | X | W | W
|  |  |  | Air assist hydrotest water draining |  | X | W | W
B-1.3.4 |  | Piping Final Reinstatement
|  |  |  | Reinstatement of all inline fragile devices and reconnection of any rotating/static equipment, according to the project procedure |  | X | I | W
|  |  |  | Remove pressure test temporaries (e.g. test blinds and temporary connections / spools, etc.) |  | X | W | I
|  |  |  | Perform visual and/or boroscopic inspection (depending on the system criticality and isometric) following strength test, dewatering and cleaning for NRV's and pressure relief items, as per SCE ITR - photo records to be kept and saved |  | X | W | H
|  |  |  | Perform final flange management inspection for all broken/disrupted flanged connections |  | X | W | I
|  |  |  | Confirm and adjust, if required, all piping spring supports for cold and hot settings, gags removal and monitoring for pipe strain |  | X | W | I
Note: NRV/TSO FAT testing records to be made available during final installation
|  |  |  | Install PSVs within 90 days of CC leaving 90 days for commissioning to put in service or under preservation |  | X | I | I
B-1.3.5 |  | Gross Air Leak Test
|  |  |  | Develop the testing plan and associated tags for all the gross air leak tests. Include definition of test media, test pressures, etc. Produce a Tracking document to be updated on a daily basis and reported accordingly |  | X | A | I
|  |  |  | Perform the gross air leak test according to approved packs method of statements |  | X | W | W
|  |  |  | Perform Intermediary Drying activities according to the established drying packs method statements (this activity can be combined with the Gross leak test packs) |  | X |  | W
B-1.3.6 |  | Tightness Testing - High pressure
|  |  |  | Develop the testing plan and associated tags for all the high pressure leak tests. Include definition of test media, test pressures, etc. Produce a Tracking document to be updated on a daily basis and reported accordingly |  | S |  | X
|  |  |  | Identify and develop all the high pressure leak test packs for the project, by preparing one method of statement per test pack with P&ID mark-ups. |  | S |  | X
|  |  |  | Prepare, supply and fabricate all the required temporary hoses, fittings, gauges, etc...and N2/Air or N2+He equipment to perform the high pressure leak test activity. Ensure that all temporary equipment is duly suitable for usage and it follows the piping rating permanent requirements. |  | S |  | X
|  |  |  | Prepare and maintain a tracking list for all permanent used test blinds required / installed (including locations) for all activities, prior to CC |  | S |  | X
|  |  |  | Perform leak testing according to approved procedures |  | S |  | X
|  |  |  | Perform any remedial works and respective retesting (can be sectioned, if possible) required as a result of leakages identified during high pressure leak test, refer to flange management procedure requirements |  | X | A | W
B-1.3.7 |  | Drying and Inerting
|  |  |  | Develop the drying plan and associated tags for all the drying packs. Include definition of drying media. Produce a Tracking document to be updated on a daily basis and reported accordingly |  | S |  | X
|  |  |  | Prepare, supply and fabricate all the required temporary hoses, fittings, gauges, etc...and N2/Air or N2+He equipment to perform the drying activity. Ensure that all temporary equipment is duly suitable for usage and it follows the piping rating permanent requirements. |  | S |  | X
|  |  |  | Prepare, supply and fabricate all the required temporary hoses, fittings, gauges, etc...and N2/Air or N2+He equipment to perform the high pressure leak test activity. Ensure that all temporary equipment is duly suitable for usage and it follows the piping rating permanent requirements. |  | S |  | X
|  |  |  | Perform drying and inerting according to the project approved procedures and specifications |  | S |  | X
|  |  |  | Remove leak test temporaries (e.g. test blinds and temporary connections / spools, etc.) and perform flange management according to project approved procedure |  | S | W | X
C-1 | All Equipment
C-1.1 |  | General
|  |  | Check proper connection of auxiliary systems (lube oil, purge, quench, balance, cooling, etc.) |  |  | X | W
|  |  | Issue request and execute final inspection for equipment Box-up prior and post: catalyst, chemical or any other first filling, if applicable. Record and provide to COMPANY photographic and video record |  |  | X | H | H | H
C-1.2 |  | Receipt and Installation
|  |  |  | Check all received equipment against specifications. Inspect and confirm no damage during transit. |  | X |  | I
|  |  |  | Remove all internal packing straps and braces |  | X
|  |  |  | For major equipment, mobilise vendor representative to confirm proper installation, in accordance with Vendor project documentation |  | X | A
|  |  |  | Ensure preservation log is available and duly populated, such log must be shared with CSU Team, prior to handover |  | X |  | A
|  |  |  | Supply all consumables and perform all preservation activities as required for all Equipment's, as per vendor guidelines and project specifications. |  | S | I | X
C-1.3 |  | Vendor Packaged Equipment
|  |  |  | Site Inspection of vendor supplied items for internals installation, temporary shipping supports removal and cleanliness |  | X | W
|  |  |  | Ensure Skid mounted Piping, Vessels, Equipment installed, bolted and supported correctly, externally clean and undamaged. |  | X | H
C-1.4 |  | Towers , Vessels and slug Catcher
C-1.4.1 |  | During Construction, up to Construction Completion
|  |  |  | Provide all temporary access required for inspection, installation, filling purpose |  | X | W
|  |  |  | Open all Manways, clean out all vessels, trays, manways or any other openings and prepare for final inspection |  | X | W
|  |  |  | Inspect all internals and/or perform a mock-up installation test, prior to start the internals installation inside of the equipment |  | X | H | H
|  |  |  | Install all internals such as: distributors, demister separators, packing, etc. as per vendor and project specifications |  | X | H | W
|  |  |  | Perform all the required tests prior to achieve Construction Completion, according to specifications, such as: tray leakage test, levelling adjustment, etc. |  | X | H | H
|  |  |  | Correct any defects, damages found during testing, even if proved it come from Vendors fabrication premises |  | X | H
|  |  |  | Install any linings and carry out required curing, if applicable |  | X | W | W | W
|  |  |  | De-blind equipment where applicable |  | S | W | X
C-1.4.2 |  | During Commissioning
|  |  |  | Supply and install inert packing materials for bed supporting purpose (e.g. balls, resins, sand, desiccants, etc.), if applicable |  | X | I | H
|  |  |  | Load catalysts, chemicals and other first fills, if applicable |  | X | I | H
C-1.5 |  | Storage Tanks
C-1.5.1 |  | During Construction, up to Construction Completion
|  |  |  | Install, connect, calibrate and test any internals such as ladders, gauges, and others that require field installation or assembly |  | X | W
|  |  |  | Perform tank cleaning and, if required, hydrotest the tanks (tank strapping to be applied if required). Ensure to disconnect all piping and instrument connections, prior to test. |  | X | W
|  |  |  | Verify and control roof raising requirements, monitoring and approved procedures |  | X | W
|  |  |  | Perform Internal final visual inspection and provide a Photographic record prior to Tank Closure |  | X | H | H | W
C-1.5.2 |  | During Commissioning
|  |  |  | Where applicable inspect, calibrate and test tank cathodic protection system. |  |  |  | X
|  |  |  | Filling tank with first fills and perform dynamic commissioning runs to complete level instrument calibration and SIF testing according to project procedure and specifications |  |  |  | X
C-1.6 |  | Shell and Tube Heat Exchangers
|  |  |  | Perform equipment inspection and, if possible, perform boroscope for internal inspection and cleanliness verification |  | X | W
C-1.7 |  | Air Fin Coolers
C-1.7.1 |  | During Construction, up to Construction Completion
|  |  |  | Level base plates, blocks, rails, sole plates, etc., and/or the equipment as instructed by the supplier |  | X | I
|  |  |  | Check and inspect level |  | X | I
|  |  |  | Inspect sheaves and belts for alignment and tension / adjust as required (belts to be removed if fans are to be left on off mode for extended periods of time, to be decided by COMPANY CSU and Ops) |  | X | I | I
|  |  |  | Check for header movement clearance and removal of shipping clips. |  | X | I | I
|  |  |  | Tube externals and fins are clean and undamaged |  | X | I | I
|  |  |  | Perform initial charge of lubricants |  | X | I
|  |  |  | Check for blade tip clearance and adjust blade settings |  | X | I | I
C-1.7.2 |  | During Commissioning
|  |  |  | Check for direction of rotation and adjust fan rotation, vibration switches, blade settings and control system |  |  |  | X
|  |  |  | Check applicable trip and shutdown mechanisms |  |  |  | X
|  |  |  | Perform Uncoupled Run ( Solo-Run), if applicable |  |  |  | X
|  |  |  | Running of Air Coolers as part of System Dynamic Commissioning Procedure, as per vendor required duration and project requirements |  |  |  | X
C-1.8 |  | Centrifuge
C-1.8.1 |  | During Construction, up to Construction Completion
|  |  |  | Level base plates, blocks, rails, sole plates, etc., and/or the equipment as instructed by the supplier |  | X | W
|  |  |  | Check warning signs and interlocks |  | X | W
|  |  |  | Inspect belts for alignment and tension, adjust as required |  | X | W
|  |  |  | Make cold alignment according to supplier's tolerances and specifications and record thru the respective ITR |  | X | W
C-1.8.2 |  | During Commissioning
|  |  |  | Fill lube oil system with correct lubricant or Install initial charge of lubricants, if applicable |  |  |  | X
|  |  |  | Check applicable mechanical and electrical trip and shutdown mechanisms |  |  |  | X
|  |  |  | Charge and pressurise Seal Systems as applicable |  |  |  | X
|  |  |  | Check for vibration switches correct installation and wiring |  |  |  | X
|  |  |  | Check applicable trip and shutdown mechanisms |  |  |  | X
|  |  |  | Perform Uncoupled Run ( Solo-Run to check direction of rotation), as applicable |  |  |  | X
|  |  |  | Running of equipment as part of System Dynamic Commissioning Procedure |  |  |  | X
C-1.9 |  | Electric Heaters
C-1.9.1 |  | During Construction, up to Construction Completion
|  |  |  | Level base plates, blocks, rails, sole plates, etc., and/or the equipment as instructed by the supplier |  | X | W
|  |  |  | Verify ingress protection is suitable for area. |  | X | W
|  |  |  | Check all power and control circuit connections are correct, tight and cable markings fitted. |  | X | W
|  |  |  | Check for proper circuit identification and in line with the single line diagram, provided by vendor |  | X | W
|  |  |  | Connect Earth bar and earthing and check earth path resistance. |  | X | W
|  |  |  | Perform Test insulation resistance and continuity for each heating element |  | X | W
C-1.9.2 |  | During Commissioning
|  |  |  | Confirm fuse / CCB rating at Switch Board feeder cubicle is correct. |  |  |  | X
|  |  |  | Confirm control equipment operating correctly. |  |  |  | X
|  |  |  | Confirm correct function of all the alarms and trips. |  |  |  | X
|  |  |  | Perform pre-energization insulation resistance tests on heater elements and associated power circuits. |  |  |  | X
|  |  |  | Energise Heater and Confirm heater response is satisfactory over temperature control range |  |  |  | X
|  |  |  | Running of equipment as part of System Dynamic Commissioning Procedure |  |  |  | X
C-1.10 |  | Fired Heaters
C-1.10.1 |  | During Construction, up to Construction Completion
|  |  |  | Verify, as a minimum: (additional checks may be required according to vendor guidelines) |  | X | W
[5 empty] | Internal coating of the casing. | X | W
[5 empty] | Combustion chamber refractory installation as per design. | X | W | W
[5 empty] | Burner alignment | X | W | W
[5 empty] | Internal cleanliness of the combustion chamber and flue ways | X | W | W
[5 empty] | Internal alignment of the individual “flexi tubes” under cold conditions | X | W
[5 empty] | Internal alignment of the flame detectors | X | W
[5 empty] | Skin temperatures fixation and adjustment verification | X | W | W
[5 empty] | Freedom of movement for flexi tubes and associated purge system pipe work | X | W
[5 empty] | Correct clearance and freedom of movement for expansion of all convection section tubes | X | W
C-1.10.2 |  | During Commissioning
|  |  |  | Prepare and execute Cleaning activities for the following: |  | S |  | X
[5 empty] | Combustion chamber | S |  | X
[5 empty] | all fuel lines and process lines | S |  | X
[5 empty] | the combustion air system | S |  | X
[5 empty] | chemical cleaning, passivation and subsequent inspection of system, if applicable | S |  | X
|  |  |  | Test fans, including individual air supply to each burner. |  |  |  | X
|  |  |  | Check correct movement of dampers, etc. Manually check registers and dampers for proper operation and settings adjust if necessary |  |  |  | X
|  |  |  | Check applicable trip and shutdown mechanisms |  |  |  | X
|  |  |  | Perform Refractory dry-out by temporary or permanent means, subject to Vendor requirements |  | S |  | X
|  |  |  | Issue and execute the final equipment box-up (2 inspections maybe applicable prior to dry out and post dry out) |  | S | I | X | H
|  |  |  | Running of Equipment as part of System Dynamic Commissioning Procedure (perform final checkings such as hangers free movement, burner boxes) |  |  |  | X
C-1.11 |  | Pumps
C-1.11.1 |  | During Construction, up to Construction Completion
|  |  |  | Erect, assemble and install equipment in accordance with project specifications and vendor guidelines |  | X | W
|  |  |  | Check all equipment for "soft-foot" (all support feet should be bearing weight) and correct any deficiency. Check base plates and soleplates for alignment and inspect for grout quality |  | X | W
|  |  |  | Inspect and perform systems for cleanliness, remove any preservation compounds, greases and oils from surfaces, including the ones cleaned by third parties (suppliers, sub-contractors, etc.). Perform cleaning, as required |  | X | W
|  |  |  | Perform cold alignment to supplier's tolerances and specifications and record |  | X | W
C-1.11.2 |  | During Commissioning
|  |  |  | Supply, fill and perform lube and seal oil flushing activities as per project approved procedure, third party can be envisaged |  |  |  | X
|  |  |  | Verify and perform all ICSS SAT, loop checks and FAT final validation |  |  |  | X
|  |  |  | Charge and pressurize Seal Systems with appropriate gas, verify and correct for any leakage, as applicable |  |  |  | X
|  |  |  | Perform Compressor Un coupled Run (Solo-Run for driver rotation and driven equipment), if applicable |  |  |  | X
|  |  |  | Perform Hot alignment to supplier's tolerances and specifications and record |  |  | I | X
|  |  |  | Run the Pump as part of System Dynamic Commissioning Procedure |  |  |  | X
C-1.12 |  | Compressors
C-1.12.1 |  | During Construction, up to Construction Completion
|  |  |  | Check all equipment for “soft foot” (all support feet should be bearing weight) and correct any deficiency. Check base plates and soleplates for alignment and inspect for grout quality. |  | X | W | I
|  |  |  | Inspect and perform systems for cleanliness, remove any preservation compounds, greases and oils from surfaces, including the ones cleaned by third parties (suppliers, sub-contractors, etc.). Perform cleaning, as required and as per Vendor requirements/recommendations |  | X | W | W
|  |  |  | Supply and install permanent strainer or start-up strainer, as required. |  | X | W | I
|  |  |  | Complete compressor assembly by installing all the vendor shipped loose items, such as: mechanical seals, packing, strainers, cartridges, vibration probes, etc. |  | X | W | I
|  |  |  | Perform cold alignment to supplier's tolerances and specifications and record |  | X | W | H
|  |  |  | Complete or repair any insulation within Vendor supplied items |  | X | W
|  |  |  | Install coupling, once Solo run has been completed |  | X | W | W
C-1.12.2 |  | During Commissioning
|  |  |  | Supply, fill and perform lube oil flushing, cooling fluid flushing activities as per project approved procedures |  |  |  | X
|  |  |  | Approve final lube oil/sealing oil and coolant cleanliness, as per project and vendor requirements |  | S |  | X
|  |  |  | Charge and pressurize Seal Systems with appropriate gas, verify and correct for any leakage, as applicable |  |  |  | X
|  |  |  | Perform Compressor Un coupled Run (Solo-Run for driver rotation and driven equipment), if applicable |  |  |  | X
|  |  |  | Prepare and execute Compressor N2 Run, if applicable and under vendor supervision |  |  |  | X
[5 empty] | Reciprocating compressors an air cleaning run with hot bypass/antisurge valves removed |  |  | X
|  |  |  | Run the Compressor as part of System Dynamic Commissioning procedure, as per vendor requirements |  |  |  | X
|  |  |  | Clean all strainers during the dynamic commissioning activities, if required to do so |  |  |  | X
|  |  |  | For reciprocating compressors, rotate compressor by barring and confirm rod run out and smooth operation. |  |  |  | X
C-1.13 |  | Gas Turbine Generators and Compressors
C-1.13.1 |  | During Construction, up to Construction Completion
|  |  |  | Check all equipment for “soft foot” (all support feet should be bearing weight) and correct any deficiency. Check base plates and soleplates for alignment and inspect for grout quality. |  | X | W | I
|  |  |  | Inspect and perform systems for cleanliness, remove any preservation compounds, greases and oils from surfaces, including the ones cleaned by third parties (suppliers, sub-contractors, etc.). Perform cleaning, as required and as per Vendor requirements/recommendations |  | X | W | I
|  |  |  | Supply and install permanent strainers and/or start-up strainers, as required. |  | X | W | I
|  |  |  | Complete Gas turbine generators assembly by installing all the vendor shipped loose items, such as: mechanical seals, packing, strainers, cartridges, vibration probes, etc. |  | X | W | I
|  |  |  | Check Combustion Air Intake and air exhaust ducting/Silencer correctly installed. |  | X | W | I
|  |  |  | Check GTG Enclosure correctly assembled, all penetrations sealed. |  | X | W | I
|  |  |  | Inspect and perform systems for cleanliness, remove any preservation compounds, greases and oils from surfaces, including the ones cleaned by third parties (suppliers, sub-contractors, etc.). Perform cleaning, as required |  | X | W | W
|  |  |  | Perform power transmission couplings cold alignment as per vendor tolerances and specifications and record |  | X | W | H
|  |  |  | Complete or repair any insulation within Vendor supplied items, even if lost during erection phase during construction |  | X | W | I
|  |  |  | Install coupling once Solo run has been completed |  | X | W | W
C-1.13.2 |  | During Commissioning
|  |  |  | Supply, fill and perform lube oil flushing, cooling fluid flushing activities as per project approved procedures, third party can be envisaged |  |  |  | X
|  |  |  | Approve final lube oil/sealing oil and coolant cleanliness, as per project and vendor requirements |  |  |  | X
|  |  |  | Charge and pressurize Seal Systems with appropriate gas, verify and correct for any leakage, as applicable |  |  |  | X
|  |  |  | Perform Compressor Un coupled Run (Solo-Run for driver rotation and driven equipment), if applicable |  |  |  | X
|  |  |  | Prepare and execute Compressor N2 Run, if applicable and under vendor supervision |  |  |  | X
|  |  |  | All temporary piping spools or any other material requirements to be engineered, supplied and installed/removed, accordingly |  |  |  | X
|  |  |  | Run the Gas Turbine Generator as part of System Dynamic Commissioning procedure (procedure to reflect two distinct phases: one without hydrocarbons and the next with hydrocarbons) |  |  |  | X
|  |  |  | Clean all strainers during the dynamic commissioning activities, if required to do so |  |  |  | X
C-1.14 |  | Diesel Engines Driven Equipment
C-1.14.1 |  | During Construction, up to Construction Completion
|  |  |  | Level base plates, blocks, rails, sole plates, etc. as instructed by supplier |  | X | W
|  |  |  | Grout-in equipment as required by project specifications |  | X | W
|  |  |  | Check all equipment for "soft-foot" (all support feet should be bearing weight) and correct any deficiency. Check base plates and soleplates for alignment and inspect for grout quality |  | X | W | I
|  |  |  | Inspect and perform systems cleaning, remove any preservation compounds, greases and oils from surfaces, including the ones cleaned by third parties (suppliers, sub-contractors, etc.). Perform cleaning for the diesel lines and tank by flushing the system with process fluid, same process for water system. |  | X | W | W
|  |  |  | Complete Diesel engines assembly by installing all the vendor shipped loose items, such as: mechanical seals, packing, strainers, cartridges, vibration probes, exhaust system, etc. |  | X | W | I
|  |  |  | Perform cold alignment to supplier's tolerances and specifications and record |  | X | W | H
|  |  |  | Perform proper connection of all auxiliary systems, follow project flange management requirements (lube oil, purge, quench, balance, cooling, etc.) |  | X | W | I
|  |  |  | Supply and install permanent strainer or start-up strainer, as required. Temporary mesh on top of the permanent strainer can also be envisaged, if CSU/OPS decide so. |  | X | W | I
|  |  |  | Complete or repair any insulation within Vendor supplied items, even if not available |  | X | W
|  |  |  | Install coupling, once Solo run has been completed |  | X | W | W
C-1.14.2 |  | During Commissioning
|  |  |  | Supply and fill the system with all the first fills: such as diesel, water, cooling fluid, etc. etc... |  |  |  | X
|  |  |  | Supply, fill and perform Diesel flushing activity as per project approved procedures, third party can be envisaged |  |  |  | X
|  |  |  | Perform Compressor Un coupled Run (Solo-Run for driver rotation and driven equipment), if applicable |  |  |  | X
|  |  |  | Perform Dry Trip Testing on the Overspeed and the Fast Stop facility |  |  |  | X
|  |  |  | Commissioning and start-up of Diesel Engine in accordance to Vendor guidelines |  |  |  | X
|  |  |  | Carry engine unloaded/Loaded testing and Check governor ability to control engine speed |  |  |  | X
|  |  |  | Run the Diesel Generator as part of System Dynamic Commissioning procedure |  |  |  | X
|  |  |  | Clean all strainers during the dynamic commissioning activities, if required to do so |  | S |  | X
C-1.15 |  | Filters & Coalescer
C-1.15.1 |  | During Construction, up to Construction Completion
|  |  |  | Inspect and perform systems cleaning, remove any preservation compounds, greases and oils from surfaces. |  | X | W | I
|  |  |  | Complete full assembly by installing all the vendor shipped loose items and prepare for elements installation (scaffolding access, or any other requirement) |  | X | W
C-1.15.2 |  | During Commissioning
|  |  |  | Supply and install final filter bed/media (cartridge, activated carbon, sand, rock, crushed material, etc.) |  |  |  | X
|  |  |  | Perform Equipment Dynamic Commissioning activities as per project procedures |  |  |  | X
C-1.16 |  | Flares , Incinerator and thermal oxidiser
C-1.16.1 |  | During Construction, up to Construction Completion
|  |  |  | Confirm that Flare pilot assembly is complete and secure. |  | X | W
|  |  |  | Install and Test the Flare tip removal equipment (if applicable) |  | X | W
|  |  |  | Install and perform non-operational Testing for all the Flare supporting systems (including: aeroalert lights, wind sock, flame detectors, junctions boxes connectivity, heat covers, etc.) |  | X | W
|  |  |  | Conduct all non-operating checks and sequencing as per the supplier's recommendation. |  | X | W
|  |  |  | During Flare erection, check the piping cleaning and integrity by section |  | X | W | I
C-1.16.2 |  | During Commissioning
|  |  |  | Perform drying and purging operations. |  | S | S | X
|  |  |  | Test Run of Air Blowers ( If applicable) |  |  |  | X
|  |  |  | Perform all Dry functional testing of Flare Package ( Without Fuel gas) |  |  |  | X
|  |  |  | Perform all functional testing of Flare Ignition system utilising Temporary Gas Arrangement ( Propane Bottles, if applicable) |  |  |  | X
|  |  |  | Perform Functional testing of Flare Package and Flare Ignition Package utilising Plant Fuel gas |  |  |  | X | W
C-1.17 |  | Handling Equipment, Cranes, Winches and Hoists
C-1.17.1 |  | During Construction, up to Construction Completion
|  |  |  | Perform mechanical checks, end stops suitability, lubricate and adjust all equipment as per Vendor recommendations and project specifications |  | X | W
|  |  |  | Perform marking for Hoist beam work load and identification number, to be clearly visible from the ground |  | X | W
|  |  |  | Perform Crane/Hoist load Test and complete all certification requirements |  | X | W | W
|  |  |  | Perform crane functional test as per vendor guidelines and project procedures |  | X | W | W
|  |  |  | Fixed Rail devices (Monorail etc.) Conduct load & functional test throughout travel length |  | X | W | W
|  |  |  | Inspect wire ropes and obtain the required and applicable certification |  | X | W
|  |  |  | Obtain all required certification and approvals from third parties and ensure any required witness parties / authorities are notified |  | X | W | W
C-1.17.2 |  | During Commissioning
|  |  |  | Perform Crane/ Winch safety and protection checks in accordance with vendor requirements and B-ITRs |  | X
|  |  |  | Check all Crane Operating Modes ( Local /Remote ; Manual / Auto ) |  | X
|  |  |  | Operate crane under no load to verify operability of unit (free of any defects) and controls |  | X |  | H
|  |  |  | Lubricate and make running adjustments during dynamic commissioning |  | X
C-1.18 |  | Weight Bridge
C-1.18.1 |  | During Construction, up to Construction Completion
|  |  |  | Check freedom of moving parts, proper function of devices to limit motion, proper direction of rotation |  | X | W
|  |  |  | Perform mechanical checks, lubricate and adjust all equipment as per Vendor recommendations and project specifications |  | X | W
|  |  |  | Supply/arrange test weights for load test and dispose of test weights after test completion |  | X | I | H
|  |  |  | Obtain all required certification and approvals from third parties and ensure any required witness parties / authorities are notified |  | X | W
|  |  |  | Perform any Calibration and un-energized Test as per vendor requirements |  | X | W
C-1.18.2 |  | During Commissioning
|  |  |  | Verify any remote control operations, acceptable frequencies & licenses ( As applicable) |  | X | W | W
|  |  |  | Perform Weight Bridge functional test and Communication tests as per vendor guidelines and project procedures |  | X | W | W
|  |  |  | Perform Weight Bridge Stability Test, repeatability, zero stability and calibration (As applicable) |  | X | W | W
C-1.19 |  | Loading equipment/Jetty Station
C-1.19.1 |  | During Construction, up to Construction Completion
|  |  |  | Check freedom of moving parts (such as loading arm), proper function of devices to limit motion, proper direction of rotation |  | X | W
|  |  |  | Test, check and verify systems according to approved procedures and ITRs |  | X | W
|  |  |  | Obtain all required certification and approvals from third parties and ensure any required witness parties / authorities are notified |  | X | W
C-1.19.2 |  | During Commissioning
|  |  |  | Perform Loading Station functional test and Communication tests as per vendor guidelines and project procedures |  | X |  | W
|  |  |  | Perform any Calibration and un-energized Testing as per vendor requirements |  | X |  | W
|  |  |  | Perform all additional Commissioning Checks as per Vendor Requirements. |  | X |  | W
|  |  |  | Conduct Loading Station dynamic commissioning and perform initial loading test |  | X |  | H
D-1 | Safety and Fire Fighting Systems
|  |  | All testing temporary requirements to be planned and supplied for the respective activity |  |  | X
D-1.1 |  | During Construction, up to Construction Completion
|  |  |  | Complete full assembly by installing all the vendor shipped loose items and assembling the system as per the project documentation |  | X | I
|  |  |  | Provide safety and fire fighting equipment certificates and execute the installation with a certified personal for the specific item, as required |  | X | I
|  |  |  | Supply and install all the signage within the plant facilities, as per project requirements (fluid code, exit, energized stickers, etc.) |  | X | W
|  |  |  | Supply, installation and validate certification of loose safety equipment ( such as: fire extinguishing, SCBA,etc.) |  | X | W
[5 empty] | Support installation, as per project procedures | X | I
[5 empty] | Supply and installation according to the commissioning and start-up needs (as close as possible of sailaway, start-up and/or SH phase, to be defined along with COMPANY Ops (GOO)) | X |  | I | A
|  |  |  | Install clear and legible safety and fire fighting equipment instruction labels as applicable |  | X | W
|  |  |  | Confirm safety and fire fighting equipment cabinets installation, ensure door and latching mechanism is operable. |  | X | W
|  |  |  | Complete Installation of water connections and drains in accordance to supplier's recommendation and project specifications |  | X | I
|  |  |  | Check and confirm all safety and fire fighting equipment for ease of operation |  | X | I
|  |  |  | Install barrier posts around fire monitors, hydrants and cabinets as per project specifications |  | X | I
|  |  |  | Paint emergency escape routes according to project specifications |  | X | W
D-1.2 |  | During Commissioning
|  |  |  | Supply and loading the first fill of all chemicals, powders and other first fills, as per project specifications |  |  |  | X
|  |  |  | Perform commissioning activities by testing all the commissionable systems according to the project approved procedure. Provide a second recharge, whenever applicable and required as per the testing plan. |  |  |  | X
[5 empty] | Execute shower / eyebath testing and confirm the spray pattern and coverage is correct. |  |  | X | W
[5 empty] | Execute fire monitor spray pattern test with firewater supply and confirm performance as per project specifications | S |  | X | W
[5 empty] | Execute foam / CO2 / sprinkler systems testing and confirm performance as per project Specifications | S |  | X | W
[5 empty] | Execute deluge package testing and confirm performance as per project specifications | S |  | X | W
[5 empty] | Execute dry powder and engine systems testing and confirm performance as per project specifications | S |  | X | W
E-1 | HVAC Systems
E-1.1 |  | During Construction, up to Construction Completion
|  |  |  | Complete full assembly by installing all the vendor shipped loose items and assembling the system as per the project documentation |  | X | I
|  |  |  | For piping, mechanical, instrumentation and electrical scope of work, within HVAC supply or work scope, follow exactly the same requirements at a discipline level (refer to section B, C, G and H of this matrix) |  | X | I
|  |  |  | Complete all duct work in accordance with design drawings and project specifications delivering clean and tight systems |  | X | I
[5 empty] | Clean and test air ducts and check joints for leaks in accordance to project specifications | X | H | W
[5 empty] | Install all flexible joints and ensure all joints and Instrument insertions are sealed | X | I
[5 empty] | Air flow direction and duct identification labels correctly fitted as per project specifications | X | I
[5 empty] | Ensure adequate support and anti-vibration mountings are fitted | X | I
|  |  |  | Complete all Insulation works |  | X | I
|  |  |  | Provide and install air filters |  | X | I
|  |  |  | Charge refrigerant and air conditioning systems in accordance with suppliers’ instructions, if applicable |  | X | W
E-1.2 |  | During Commissioning
|  |  |  | Perform dynamic commissioning operation and check output of systems |  |  |  | X
|  |  |  | Perform HVAC system control testing and verification for all control and alarms, under vendor supervision if required |  |  |  | X
|  |  |  | Testing, adjusting and balancing HVAC units, fans adjustment for air and hydraulic systems, as per vendor recommendations and based on the different sections of this document. |  |  |  | X
|  |  |  | Operate and conduct performance test on HVAC |  |  |  | X
F-1 | Underground Installations: Sumps, Sewers, etc.
F-1.1.1 |  | During Construction, up to Construction Completion
|  |  |  | Verify that buried pipe is properly cleaned, coated, supported, and pressure / leak tested before burial according to specifications |  | X | W | W
|  |  |  | Ensure that underground valves ( Buried PIVs and Non Buried in Pits) are operable |  | X | W
|  |  |  | Ensure all rodding points are accessible |  | X | W
|  |  |  | Leave all welded joints exposed in underground piping until specified testing is complete |  | X | W
|  |  |  | Perform testing of welded joints in underground piping that have not been shop tested |  | X | W
|  |  |  | Cover joints after completion of testing |  | X | W
Note: provide proper temporary protection of the sewer system to avoid contamination or pollution
F-1.1.2 |  | During Commissioning
|  |  |  | Remove Temporary Strainers and all temporaries after Commissioning |  |  |  | X
|  |  |  | Testing of Open Drain system piping by filling and monitoring level |  |  |  | X
|  |  |  | Inspect & Clean for dirt and debris prior to final closure, before system in service |  |  |  | X
|  |  |  | Flush sewer system |  |  |  | X
|  |  |  | Fill seals in sewer system |  |  |  | X
G-1 | Electrical
G-1.1 |  | General to all Electrical Equipment
|  |  |  | Verify equipment calibration and settings in accordance with design documentation |  | S |  | X
|  |  |  | Execute PCCS Loop and System Testing |  |  |  | X | W
G-1.1.1 |  | During Construction, up to Construction Completion
|  |  |  | Provide duly trained personal for COMPEX/ATEX installation within the plant. |  | X | A
|  |  |  | Connect to earth and bond equipment in accordance with vendor and project specification |  | X | I
|  |  |  | Perform the required checks and tests of the equipment, as required by project specification and procedures |  | X | I
|  |  |  | Inspect and perform systems cleaning, verify for any preservation compounds. |  | X | I
|  |  |  | Implement equipment isolation procedure and provide warning signs for permanent systems energised prior to Construction Completion (only permitted for preservation purposes) |  | X | I | I
G-1.1.2 |  | During Commissioning
|  |  |  | Provide duly trained personal for COMPEX/ATEX installation within the plant. (provision of certification reports and other). |  | X | A | A
|  |  |  | Prior to energization of any electrical equipment, perform cleaning and removal of any unwanted equipment or any other item, from the area under commissioning |  | X |  | W
|  |  |  | Prepare and install all the required signage and barrication for sectioning the area under commissioning/energization, from others |  |  |  | X
|  |  |  | Perform all operational equipment functional and performance checks and tests |  |  |  | X
|  |  |  | Verify and test all equipment operating protection alarms settings, trips and shutdown systems (HV and MV only) |  |  |  | X
G-1.2 |  | Specific to Equipment under Hazardous area requirements
G-1.2.1 |  | During Construction, up to Construction Completion
|  |  |  | Provision of personnel trained in various types of protection and installation practices, rules and regulations |  | X | W
|  |  |  | Perform activities to maintain equipment certification from manufacturer, through all the project |  | X | I
|  |  |  | Initial detailed inspection of equipment and installation in accordance with project standards and regulations |  | X | W
|  |  |  | Maintenance of hazardous area equipment inventory and identification tagging method |  | X | I
|  |  |  | Maintain up-to-date area classification documents showing extent and class of the hazardous areas including the zoning |  | X | I
G-1.2.2 |  | During Commissioning
|  |  |  | Maintain equipment inspection records and hazardous area certification equipment registers |  | S |  | X | I
|  |  |  | Maintain test, preservation and calibration records (incl. conducting equipment calibration) |  | S |  | X | I
G-1.3 |  | Transformers
G-1.3.1 |  | During Construction, up to Construction Completion
|  |  |  | Assemble, install and connect protective equipment |  | X | I
[5 empty] | Perform Torqueing on final connection to ceramic bushing, according to project specifications | X | H
|  |  |  | Measure and record insulation resistance for: between HV and LV and windings to earth |  | X | I
|  |  |  | Perform mechanical checks and verifications for: breather (conservator type); liquid level, gasket tightness and any surface damage, as per the requirements |  | X | I
|  |  |  | Assemble and install cooling system, if applicable |  | X | I
|  |  |  | Assemble, install - handling, storage, filling, pre-energization sampling & testing in accordance with vendor guidelines. Verify and test for oil quality for particles counting |  | X | I | W
G-1.3.2 |  | During Commissioning
|  |  |  | Perform first filling for Oil system, if applicable |  |  |  | X
|  |  |  | Perform final oil cleanliness inspection, prior to permanent energisation |  |  |  | X
|  |  |  | Perform Power System testing/Check Off-Circuit/On load tap changer (if installed) - transformer ratio and position check ATM |  |  |  | X
|  |  |  | Perform all metering, measurement and indication equipment function checks |  |  |  | X
|  |  |  | Perform all equipment functional and performance checks |  |  |  | X
|  |  |  | Perform post-energization oil sample & testing in accordance with vendor guidelines |  |  |  | X
G-1.4 |  | Switchgear Equipment (HV and LV switchgear plus busbar trunking systems)
G-1.4.1 |  | During Construction, up to Construction Completion
|  |  |  | Assemble, install and connect protective equipment according to vendor and project specifications |  | X | I
|  |  |  | Perform Bus Bars Cast resin joints by mixing and pouring (ensure vendor witnessing) |  | X | I
|  |  |  | Measure and record insulation resistance between: phase to phase and phase to earth |  | X | W
|  |  |  | Execute and record bolts/nuts tightening, in accordance to vendor and project requirements for power systems (calibrated and certified torque wrench and dynamometric key to be used for inspection purpose) |  | X | W
|  |  |  | Execute and record BusBar torqueing values, in accordance to vendor and project requirements (calibrated and certified torque wrench and dynamometric key to be used for inspection purpose) |  | X | H
|  |  |  | Execute and record conductivity tests between adjacent cubicle spouts and low resistance tests, across busbar connections |  | X | I
G-1.4.2 |  | During Commissioning
|  |  |  | Perform overall conductivity / low resistance test |  |  |  | X
|  |  |  | Perform and record Power System testing, including Hi-Pot ( Pressure) Test at the appropriate Voltage Level to the system, as defined in project requirements |  |  |  | X
|  |  |  | Perform and record the Protection relays settings testing, in accordance with vendor instructions, ensure vendor witnessing |  |  |  | X
|  |  |  | Perform and record Intertrips and injection tests, as required |  |  |  | X
|  |  |  | Perform and record metering, measurement and indication equipment functionality checks |  |  |  | X
G-1.5 |  | Cables and Cabling
G-1.5.1 |  | During Construction, up to Construction Completion
|  |  |  | Providing Competent and fully trained personnel for HV/LV cable installation, jointing and testing, in accordance with vendor guidelines and project specifications |  | X | W
|  |  |  | Install and tag all power cables, control cables, intrinsically safe and non-intrinsically safe cables, in accordance with project procedures |  | X | I
|  |  |  | Identification of cable joint locations, perform resistance test and record the results, in accordance with vendor requirements and project procedures |  | X | I
|  |  |  | Perform continuity and insulation resistance tests in accordance with project procedures |  | X | W
|  |  |  | Perform and record tests of all electrical signals and alarm wiring for continuity, correct source of power and polarity |  | X | W
|  |  |  | Perform and record HV cable Hi-Pot test, according to project requirements |  | X | W
|  |  |  | Perform cable termination on all main lugged power feeder cables, according to project requirements |  | X | W
G-1.5.2 |  | During Commissioning
|  |  |  | Perform and record pre-energization insulation resistance tests for HV and LV power cables, prior to Permanent energization |  |  |  | X
|  |  |  | Prior energization perform final checks and record for: final termination, torqueing, phasing and conductivity low resistance tests on all main lugged power feeder cables |  |  |  | X
G-1.6 |  | Earthing and bonding system
G-1.6.1 |  | During Construction, up to Construction Completion
|  |  |  | Install and connect the lightning protection equipment and connect it to the plant earthing system network |  | X | I
|  |  |  | Measure and record earth resistance of overall earthing system, resistance value shall not exceed project specification |  | X | I
|  |  |  | Measure and record earth electrode resistance values |  | X | I
|  |  |  | Measure and record continuity between earth electrode, plant neutral and plant earth loop |  | X | I
|  |  |  | Perform continuity checks and tests between switchboards, transformers, substation and earth bars main ring |  | X | I
|  |  |  | Measure and record earth loop impedance of all power and convenience outlets |  | X | I
|  |  |  | Perform spot check and record electrical and non-electrical equipment earthing bonding resistance value |  | X | W
G-1.6.2 |  | During Commissioning
|  |  |  | Spot check and record electrical and non-electrical equipment earthing bonding resistance value |  |  |  | X
|  |  |  | Perform and record equipment functional and performance checks on earth fault protection devices |  |  |  | X
G-1.7 |  | Neutral Earthing Resistors (NER), Neutral Earthing Transformers (NET), Current Transformers (CT) and Voltage Transformers (VT)
G-1.7.1 |  | During Construction, up to Construction Completion
|  |  |  | Install all equipment (NER, NET, CT and VT) in accordance with vendor requirements and project specifications |  | X | I
|  |  |  | Check and record NER, NET, CT, VT and relays for size, rating, connection integrity and frame earthing, in accordance with project specification |  | X | I
|  |  |  | Obtain, verify and record NER, NET, CT, VT and relays vendor test certificates and performance data and cross check with installed equipment/nameplate |  | X | I
G-1.7.2 |  | During Commissioning
|  |  |  | Perform and record polarity, saturation curve & winding resistance tests |  |  |  | X
|  |  |  | Verify and record all equipment settings for protection alarms, trips and shutdown systems |  |  |  | X
|  |  |  | Perform metering, measurement and indication equipment function checks |  |  |  | X
|  |  |  | Perform and record all equipment functional and performance checks and tests |  |  |  | X
G-1.8 |  | Buildings - Substations, Electrical rooms, Local Equipment or Instrument Rooms, Enclosures
For all general disciplines installation and verification within a building follow the discipline requirements within this DoR apply.
G-1.8.1 |  | During Construction, up to Construction Completion
|  |  |  | Applicable to any Building, room or enclosure, installation, verification and control for: |  | X | I
[5 empty] | Sealing control for any opening, doors or wall crossing/penetration | X | I
[5 empty] | connecting floors are levelled and breakers slide out properly | X | I
[5 empty] | lighting and convenience outlets, according to the project requirements | X | I
[5 empty] | normal, emergency and escape lighting systems installation, as per project documentation | X | I
[5 empty] | HVAC systems (Electrical Panels/Components only) | X | I
[5 empty] | earthing and equipment bonding | X | I
[5 empty] | fire protection systems | X | I
[5 empty] | gas detection systems | X | I
[5 empty] | electrical safety equipment, signage, eye wash stations and rubber matting as per project specification | X | I
|  |  |  | Verify electrical rooms are dust free and that no other equipment's are temporarily stored within any room or enclosed area |  | X | W
|  |  |  | Perform any test, preservation and/or calibration requirements, even if within vendor scope of supply |  | X | W
G-1.8.2 |  | During Commissioning
|  |  |  | Perform and record all functional and performance checks on fire protection and gas detection systems |  |  |  | X
|  |  |  | Perform and record pre-energization insulation resistance tests on all building electrical system power circuits |  |  |  | X
|  |  |  | Perform and record all functional checks and tests for building electrical system |  |  |  | X
|  |  |  | Perform and record all functional checks and tests for building HVAC systems (summer and winter testing) |  |  |  | X
|  |  |  | Perform Building tightness test and record the leakage rate, ensure that it follows project safety requirements |  |  |  | X
G-1.9 |  | UPS System
G-1.9.1 |  | During Construction, up to Construction Completion
|  |  |  | Install, perform all connections, verify and record equipment installation according to project requirements and dedicated discipline ITR's |  | X | W
G-1.9.2 |  | During Commissioning
|  |  |  | Perform and record pre-energization insulation resistance tests on all power circuit systems |  |  |  | X
|  |  |  | Perform and record equipment functional and performance checks and tests |  |  |  | X
|  |  |  | Verify and record the settings for equipment protection alarms, trips and shutdown systems |  |  |  | X
G-1.10 |  | Power electronics (Variable Speed Drives, control panels etc.)
G-1.10.1 |  | During Construction, up to Construction Completion
|  |  |  | Install, perform all connections, verify and record equipment installation according to project requirements and dedicated discipline ITR's |  | X | I
G-1.10.2 |  | During Commissioning
|  |  |  | Perform and record pre-energization insulation resistance tests on all power circuit systems |  |  |  | X
|  |  |  | Perform and record equipment functional and performance checks and tests |  |  |  | X
|  |  |  | Verify and record the settings for equipment protection alarms, trips and shutdown systems |  |  |  | X
G-1.11 |  | Batteries and Battery Chargers
G-1.11.1 |  | During Construction, up to Construction Completion
|  |  |  | Install, perform all connections, verify and record equipment installation according to project requirements and dedicated discipline ITR's |  | X | W
G-1.11.2 |  | During Commissioning
|  |  |  | Perform and record pre-energization insulation resistance tests on all power circuit systems |  |  |  | X
|  |  |  | Perform and record equipment functional and performance checks and tests, including loading trip settings verification |  |  |  | X
|  |  |  | Verify and record the settings for equipment protection alarms, trips and shutdown systems |  |  |  | X
G-1.12 |  | Lighting and power sockets systems
G-1.12.1 |  | During Construction, up to Construction Completion
|  |  |  | Supply, install and maintain sufficient temporary lighting and facilities (such as generators, diesel, etc.), as required, to support Construction Completion activities |  | X | I
|  |  |  | Supply, install and maintain sufficient temporary facilities for mechanical activities completion, such as power supply temporary boards, sockets, generators , fire extinguishers, etc) |  | X | I
|  |  |  | In case the designed facilities are considered not sufficient for a safe and permanent operation requirements, COMPANY is entitled to request CONTRACTOR to modify the installation and make whatever is required until it suits for purpose, at no additional cost |  | X | I
G-1.12.2 |  | During Commissioning
|  |  |  | Perform pre-energization insulation resistance tests on all lighting power circuits |  |  |  | X
|  |  |  | Perform all equipment functional and performance checks and tests, such as lux measurement and control, according to project requirements |  |  |  | X
|  |  |  | Verify and record the operation and autonomy time of all Normal, Emergency and Escape lighting systems |  |  |  | X
G-1.13 |  | Motors and motor starters
G-1.13.1 |  | During Construction, up to Construction Completion
|  |  |  | Execute continuous preservation monitoring and control for bearing lubrication and rotation checks (consumables included), as per vendor recommendation |  | X | I
|  |  |  | Perform and record insulation resistance tests on motor windings and on motor starter |  | X | I
|  |  |  | Perform DC Hi Pot Test on high voltage starter and control circuits |  | X | W
|  |  |  | Check, test and record the control settings for shutdown permissive equipment's, e.g. pressure switches and flow switches. |  | X | I
G-1.13.2 |  | During Commissioning
|  |  |  | Perform and record pre-energization insulation resistance checks and tests on motor windings power circuits |  |  |  | X
|  |  |  | Perform and record all equipment functional checks and tests as per project requirements such as: vibration, one-hour runs etc. |  |  |  | X
|  |  |  | Verify and record phase sequence, polarity and motor rotation direction, as per project requirements |  |  |  | X
|  |  |  | Verify and record motor starter relay circuit, meter and control systems for continuity |  |  |  | X
|  |  |  | Verify and record the settings for equipment protection alarms, trips and shutdown systems |  |  |  | X
|  |  |  | Perform integration of equipment with project systems (EPDMS, ICSS, PMS, SCADA) |  |  |  | X
G-1.14 |  | Electrical Power Distribution Management System (EPDMS), Power Management System (PMS), SCADA (Supervisory Control and Data Acquisition) or any other similar electrical control system
G-1.14.1 |  | During Construction, up to Construction Completion
|  |  |  | Verify installation, connection and integration with electrical system, under Vendor supervision |  | X | I
G-1.14.2 |  | During Commissioning
|  |  |  | Perform pre-energization insulation resistance checks and tests on all system power circuits |  |  |  | X
|  |  |  | Perform and record all equipment functional testing, site acceptance tests, integrated tests and any vendor specified performance tests (power-up, communication, software mapping, etc.) under vendor supervision |  |  |  | X
|  |  |  | Verify and record operation settings for all equipment protection alarms, trips and shutdown systems |  |  |  | X
G-1.15 |  | Electrical heat tracing
G-1.15.1 |  | During Construction, up to Construction Completion
|  |  |  | Install, verify and control the installation, connection and integration with electrical system |  | X | I
|  |  |  | Prepare and update a correspondence table for system versus heat tracing record, for completion and handover readiness |  | X | I | I
|  |  |  | Install, control and test heat tracing control system, record the tests thru the project ITRs |  | X | I
|  |  |  | Heat tracing insulation resistance cables verification as per project procedure |  | X | I
|  |  |  | Check power supply and distribution |  | X | I
|  |  |  | Calibrate and record the settings for thermostats and temperature control boxes |  | X | I
G-1.15.2 |  | During Commissioning
|  |  |  | Perform pre-energization insulation resistance checks and tests on heat tracing power circuit |  |  |  | X
|  |  |  | Energise the system, perform and record all equipment functional and performance checks and tests |  |  |  | X
|  |  |  | Verify operation settings for all equipment protection alarms, trips and shutdown systems |  |  |  | X
G-1.16 |  | Cathodic Protection
G-1.16.1 |  | During Construction, up to Construction Completion
|  |  |  | Supply, install, check, verify and record the installation, connection and integration with electrical system |  | X | I
|  |  |  | Complete installation and connection of test stations, anodes, rectifiers, cables, terminations, labelling, and associated junction boxes |  | X | I
G-1.16.2 |  | During Commissioning
|  |  |  | Perform and record pre-energization insulation resistance checks and tests on all cathodic protection power circuits |  |  |  | X
|  |  |  | Perform and record all equipment functional testing, site acceptance tests, integrated tests and any vendor specified performance tests (power-up, communication, software mapping, etc.) under vendor supervision |  |  |  | X
|  |  |  | Verify and record operation settings for all equipment protection alarms, trips and shutdown systems |  |  |  | X
H-1 | Field Instrumentation
H-1.1 |  | Calibration (Installation (PAS / SIS / F&G )
H-1.1.1 |  | During Construction, up to Construction Completion
|  |  |  | Inspect and perform systems cleaning, remove any preservation compounds, greases and oils from surfaces. |  | X | I
|  |  |  | Supply of all consumables required for calibration purpose, until final handover phase, such as calibration gas and carrier gas bottles |  | X | I
|  |  |  | Complete full assembly by installing all the vendor shipped loose items |  | X | I
|  |  |  | Confirm all Equipment cabling / junction boxes and panels meets with correct hazardous area classification. |  | X | I
|  |  |  | Perform all offline checks and tests (de-energised) to ensure instrument operability. |  | X | I
H-1.1.2 |  | During Commissioning
|  |  |  | Perform Instrument calibration with calibrated standard testing equipment as per project procedures |  |  |  | X
|  |  |  | Monitor calibration equipment validity as well the consumables used for calibration purpose are as per project requirements |  |  |  | X
|  |  |  | Re validate the calibration certificate and testing, if expired according to project requirements |  |  |  | X
H-1.2 |  | Calibration (Metering)
H-1.2.1 |  | During Construction, up to Construction Completion
|  |  |  | Inspect and perform systems cleaning, remove any preservation compounds, greases and oils from surfaces. |  | X | I
|  |  |  | Confirm all Equipment cabling / junction boxes and panels meets with correct hazardous area classification. |  | X | W
|  |  |  | Perform any non-operating tests (de-energised) to ensure instrument operability. |  | X | I
H-1.2.2 |  | During Commissioning
|  |  |  | Perform Instrument calibration with calibrated standard testing equipment as per project procedures, under vendor witnessing and certification |  |  |  | X
|  |  |  | Monitor calibration equipment validity as well the consumables used for calibration purpose are as per project requirements |  |  |  | X
|  |  |  | Re validate the calibration certificate and testing, if expired according to project requirements |  |  |  | X
|  |  |  | Inform country regulatory authority of final pre-installation calibration of metering instrumentation. |  |  |  | X
|  |  |  | Execute final calibration check and testing of metering skid instrumentation with country regulatory authorities, as per project requirements |  |  |  | X
H-1.3 |  | Calibration for packaged supplied instrumentation
H-1.3.1 |  | During Construction, up to Construction Completion
|  |  |  | Inspect and perform systems cleaning, remove any preservation compounds, greases and oils from surfaces. |  | X | I
|  |  |  | Perform Instrument calibration with calibrated standard testing equipment as per project procedures, under vendor witnessing if required |  | X | I
|  |  |  | Maintain / replenish gauge liquids as required. |  | X | I
|  |  |  | For fragile devices like orifice plate and different type flow elements, control and record the different dimensions, tag information, sense of installation, according to project requirements, even if comprehended within a vendor supplied package |  | X | I
|  |  |  | Confirm all Equipment cabling / junction boxes and panels are properly connected and meet with correct hazardous area classification. |  | X | W
H-1.3.2 |  | During Commissioning
|  |  |  | Monitor calibration equipment validity as well the consumables used for calibration purpose are as per project requirements |  |  |  | X
|  |  |  | Re validate the calibration certificate and testing, if expired according to project requirements |  |  |  | X
|  |  |  | Maintain / replenish gauge liquids as required. |  |  |  | X
H-1.4 |  | Calibration specific to Pressure Relief and Vacuum relief systems
H-1.4.1 |  | During Construction, up to Construction Completion
|  |  |  | Identify and prepare the Project tracking register (and update up to SH) with the following information, as a minimum: testing requirements, pressure, back pressure, gas/liquid, flanges rating, pressure relief system type, etc… |  | X | W
|  |  |  | Bench Test and Calibration of relief items, including the ones within vendor packages or any other vendor scope of supply |  | X | W
Install PSV within 90 days of CC leaving 90 days for Commissioning and start -up duration
H-1.4.2 |  | During Commissioning
|  |  |  | Recalibration "shall" statement of 180 days. |  |  |  | X
Note: Calibration period must follow system handover and commissioning requirements. Meaning within 90 days prior to handover, ensuring availability and calibration validity to provide time for leak test execution or dynamic commissioning
|  |  |  | Provide list of final settings for all calibrated relief items |  |  |  | X
|  |  |  | Execute final calibration as per country regulatory authorities specific requirements |  |  |  | X
H-1.5 |  | Installation (PAS / SIS / F&G / Metering and Miscellaneous - Flow element, restriction orifice, any packaged supplied instrumentation, etc...)
H-1.5.1 |  | During Construction, up to Construction Completion
|  |  |  | Inspect and perform systems cleaning, remove any preservation compounds, greases and oils from surfaces. |  | X | I
|  |  |  | Supply and Install primary instrument and sub-components, likewise: - Instrument Tubing - Weather Protection Enclosures - Cables (See Electrical Section) |  | X | I
|  |  |  | Apply project flange management and tubing procedures for Vendor supplied or client supplied skids |  | X | W | I
|  |  |  | Check and record Field Instrumentation for correct orientation, accessibility and readability |  | X | I
|  |  |  | Confirm all Equipment cabling / junction boxes and panels are properly connected and meet with correct hazardous area classification. |  | X | W
H-1.5.2 |  | During Commissioning
|  |  |  | Re validate the calibration certificate and testing, if expired according to project requirements |  |  |  | X
|  |  |  | Coordinate and obtain country regulatory authority certification for metering instrumentation |  |  |  | X | H
H-1.6.1 |  | During Construction, up to Construction Completion
|  |  |  | Prepare, update and control all the loop checks folders. Prepare Loops folder register and tracking file for reporting purpose |  | X |  | I
|  |  |  | Check and record all terminations for proper and tight connections. |  | X | I | I
|  |  |  | Inspect all field terminal boxes prior to closure (moisture, seals, etc.) |  | X | I | I
|  |  |  | Install conduit seals |  | X | I | I
|  |  |  | Terminate system / serial cables and confirm communications with panels and consoles |  | X | I | I
H-1.6.2 |  | During Commissioning
|  |  |  | Energise instruments / signals and perform loop checks as per project procedures |  |  |  | X
|  |  |  | For specific items, such as Metering stations, inform country regulatory authority of loop checks of metering instrumentation. |  |  |  | X
|  |  |  | Verify and perform all ICSS SAT, loop checks and FAT final validation for all Control System |  |  |  | X | W
H-1.7 |  | Instrument subcomponents - Tubing
H-1.7.1 |  | During Construction, up to Construction Completion
|  |  |  | Cleanliness control and verification for tubing (PTFE is not acceptable, Loctite type only) |  | X | I
|  |  |  | Perform tubing strength test, according to process system design pressure (including supply of all testing material and elements) |  | X | I
H-1.7.2 |  | During Commissioning
|  |  |  | Include and line up all tubing connections within the HPLT boundaries, during testing |  |  |  | X
|  |  |  | Refer to Leak Testing section for the Leak testing requirements on Impulse Lines and connections |  |  |  | X
H-1.8 |  | Nucleonics Level Transmitter
H-1.8.1 |  | During Construction, up to Construction Completion
|  |  |  | Prepare and obtain all required regulatory approvals to transfer and store Nucleonics radio-active source |  | X | W
|  |  |  | Regularly Inspect and confirm integrity of Nucleonics source containment |  | X | W
|  |  |  | Install, check and verify the Source Holders and Shields on the vessels |  | X | W | I
H-1.8.2 |  | During Commissioning
|  |  |  | Install Nucleonics source containers, according to vendor procedures |  |  |  | X
|  |  |  | Perform Nucleonics Level Transmitter calibration, according to vendor procedure, including fluid fill in and drain, as required |  |  |  | X
I-1 | Analysers
|  |  | Supply and installation of all required calibration and carrier gas bottles |  |  | X
I-1.1 |  | During Construction, up to Construction Completion
|  |  |  | Site Inspection of vendor supplied items for ship loose installation, temporary shipping supports removal and cleanliness |  | X | W
|  |  |  | Ensure Skid mounted Piping, calibration bottles, Equipment installed, bolted and supported correctly, externally clean and undamaged. |  | X | I
|  |  |  | For discipline items such as: instrumentation, piping, equipment, electrical, etc, follow above described Construction ITR's requirements, as a minimum |  | X | I
I-1.2 |  | During Commissioning
|  |  |  | Complete all static commissioning and dynamic commissioning activities required as per Vendor and COMPANY requirements |  |  |  | X | W
|  |  |  | Complete all Commissioning activities required to bring packaged equipment to fully operational state (without Hydrocarbons) |  |  |  | X
J-1 | Control Systems
J-1.1 |  | Installation of Control Panels, Consoles and External Interface Equipment
J-1.1.1 |  | During Construction, up to Construction Completion
|  |  |  | Delivery of completed control systems with IFAT Completed with all interfaces to packaged tested |  | X |  |  |  | I
|  |  |  | Complete SAT at final location |  | X |  | W |  | W
|  |  |  | Develop Commissioning Test procedures to prove performance standard requirements |  | X |  | W |  | W
|  |  |  | Manage all Control Interfaces between vendors, subsuppliers and Main Automation Contractor |  | X |  | W |  | W
|  |  |  | Supply, install, check and record the installation of Control Panels (Package Equipment, Metering, etc.), consoles and external interface equipment, as per project requirements |  | X | W | I
|  |  |  | Verify that all cabinets, consoles, or other equipment are dust free |  | X | W
|  |  |  | Install, check and record all internal components and panel wiring, consoles, external wiring and External Interface Equipment, as per project requirements |  | X | I | I
J-1.1.2 |  | During Commissioning
|  |  |  | Check and testing for all installed control cable, part of the Functional and Site acceptance testing procedure |  |  |  | X | W
|  |  |  | Loop Test applicable to Telecom, Metering, and packages but not limited |  |  |  | X
X
J-1.2 |  | Control Panels, Consoles and External Interface Equipment (HMI)
J-1.2.1 |  | During Commissioning
|  |  |  | Check and test power supplies and fuses at Control Panels, Consoles and External Interface Equipment |  |  |  | X
|  |  |  | Carry out initial energisation of control panels, consoles and external interface equipment as per approved Commissioning procedures and vendor documentation. Record results. |  |  |  | X
K-1 | Dynamic Commissioning Execution
For general assistance requirements, refer to section A-11
|  |  | Check Alarm Management System (AMS) and confirm alarm management groups have been set up for use |  |  |  |  | X | W
K-1.1 |  | During Dynamic Commissioning for PAS / SIS / F&G / Metering and Miscellaneous
|  |  |  | Check segment loading / operation once all instrument / signals on network energised |  |  |  | X
|  |  |  | Check overall system loading and confirm sufficient redundancy is available as per project design specifications |  |  |  | X
|  |  |  | Install provisional loop tuning parameters to controllers. |  |  |  | X | I
|  |  |  | Carry out loop checks of complex controllers (in control mode) and check provisional loop tune parameters |  |  |  | X
|  |  |  | Simulation of system sequences against approved Control Narratives prior to equipment runs |  |  |  | X
|  |  |  | Perform Valves opening and closure timing check |  |  |  | X
|  |  |  | Carry out C&E / SIF Testing as per project procedures |  |  |  | X
|  |  |  | Carry out alignment F&G coverage checks against original design specifications |  |  |  | X
|  |  |  | Align and perform plant instrumentation / signals ready for Integrated Dry Shutdown and Complex logic testing (no fluids in pipe) |  |  |  | X | W
|  |  |  | Adjust instrument components using parameters for automatic operation of equipment as process units are charged and brought online |  |  |  | X | W
K-1.2 |  | During Dynamic Commissioning for Metering systems
|  |  |  | Check overall system loading and confirm sufficient redundancy is available as per project design specifications |  |  |  | X
|  |  |  | Perform sample and fast loops runs of the system and check calculations parameters (K Factor, temp, press, etc.) |  |  |  | X
|  |  |  | Inform country regulatory authority of metering system operation for witnessing |  |  |  | X | H
L-1 | Telecommunications
L-1.1 |  | Installation and Testing
L-1.1.1 |  | During Construction, up to Construction Completion
|  |  |  | Perform all required de-energised testing according to vendor guidelines and project specifications |  | X | I
L-1.1.2 |  | During Commissioning
|  |  |  | Perform all required energised testing according to vendor guidelines and project specifications |  |  |  | X
|  |  |  | Provide system software / licences and programme all system equipment to support system operational features as detailed within Project Specifications |  |  |  | X
L-1.2 |  | Specific Requirements
L-1.2.1 |  | Telephones and Certified Phones
|  |  |  | Perform all required energised testing according to vendor guidelines and project specifications |  |  |  | X | I
L-1.2.2 |  | PAGA Systems including Flashing beacons system
|  |  |  | Perform all required energised testing according to vendor guidelines and project specifications |  |  |  | X
|  |  |  | Complete PAGA coverage and speech transmission quality survey while plant is operating and verify against project specifications |  |  |  | X | H
L-1.2.3 |  | LAN Networks
|  |  |  | Perform all required energised testing according to vendor guidelines and project specifications (check ITR) |  |  |  | X
|  |  |  | Check the LAN socket is free from damage. |  |  |  | X
|  |  |  | Carry out a “ping” test to a known remote host. |  |  |  | X |  | W
|  |  |  | Confirm Data Port passes the “Basic Link” test to verify correct attenuation and losses |  |  |  | X |  | W
|  |  |  | Record the IP address of the remote host used and record the min/av/max round trip times (which shall be less than 1/2/4 mS for a local host). |  |  |  | X |  | W
L-1.2.4 |  | Plant Radio
|  |  |  | Carry out field strength survey of the Plant Radio system and confirm no black spots |  |  |  | X
|  |  |  | Program all radios and equipment to support system operational features as detailed in project specifications |  |  |  | X
L-1.2.5 |  | CCTV
|  |  |  | Perform all required energised testing according to vendor guidelines and project specifications (check ITR) |  |  |  | X
|  |  |  | Complete CCTV coverage and transmission quality survey while plant is operating and verify against project specifications |  |  |  | X | H
L-1.2.6 |  | IT&S
|  |  |  | Company internal IT&S systems to be properly installed and set-up prior to handover (final SH) |  |  |  |  | H | X